\

ENERGY, ENVIRONMENT AND SOCIETY

Lecture Notes

Chapter 8

Hydropower Basics and Types

Lecturer:

Associate Prof. Manchan Tiwari

2022, October

Learning Objectives of the Lecture:

To impart basic knowledge to undergraduate students on the topic of:

- Basics of hydropower

- Source of energy for hydropower

- Hydropower equation

- Types of hydropower

- Classifications of turbines

- Importance of micro hydro power in context of Nepal

## Source of Energy for Hydropower

The source of energy of hydropower is water flowing in a river. It is important to know that why the water flows continuously in a river. It is due to hydrological cycle of water which feds water in a river continuously. Hence the source of energy of hydropower can be termed as hydrological cycle in indirect terms.

## Hydrological cycle

The water cycle, also known as the hydrological cycle or the H2O cycle, describes the continuous movement of water on, above and below the surface of the Earth. The mass of water on earth remains fairly constant over time but the partitioning of the water into the major reservoirs of ice, fresh water, saline water and atmospheric water is variable depending on a wide range of climatic variables. The water moves from one reservoir to another, such as from river to ocean, or from ocean to atmosphere, by the physical processes of evaporation, condensation, precipitation, infiltration, runoff, and subsurface flow. In doing so, the water goes through different phases: liquid, solid (ice) and gas (vapor).

## Hydropower Plant

Hydropower plant is an energy system which derives its power from the flowing river system. The water is either stored in a reservoir or blocked by weir/dam from where the water is diverted through canal and/or penstock pipe to rotate a turbine in powerhouse. The rotating turbine drives generators that produce electricity. The amount of water which flows in the river and the height from which it falls (head) is directly proportional to the power capacity of hydropower. Basically in a hydropower the potential energy of the water is converted to kinetic energy in the nozzle which is then converted to mechanical energy in turbine. The mechanical energy of the turbine is converted to electrical energy by generator.

## Types of hydropower

### On the basis of capacity

- Pico-Hydro: Less than 5 kW

- Micro Hydro: 5 kW to 100 kW

- Mini Hydro: 100 kW to 1000 kW

- Small Hydro: 1000 kW to 10 MW

- Medium Hydro: 10 MW to 300 MW

- Large Hydro: Above 300 MW

### On the basis of working principal

#### Run-off river type

  - Uses water within the range of natural river flow

  - Seasonal variation of flow results in varying power production

  - No storage of water energy

#### Reservoir/Pondage type

  - Has a reservoir that enables regulating the river flow

  - Supplies power in response to the demand

  - Head may alter as per reservoir water level

#### Pump storage type

  - Has an upper reservoir and a lower reservoir

  - Generates power during peak demand

  - Pumps up water during low demand

  - Improves load factor

The hydropower can be runoff type or storage (reservoir/pondage) type. In run off type, the flowing water is directly fed in to hydropower plant where as in storage type the water from river is first brought in to a storage and then fed in to hydropower plant. The main disadvantage of run off type is that if the river flow decreases then the power output of the hydropower also decreases and in case of storage type even in the river flow decreases the storage ensures that the flow required for hydropower is met so that there is no considerable change in power output of the plant. In some cases the pump storage type is also used. In pump storage type the water from turbine exit is again pumped back in to reservoir during the low electricity demand period so as to meet the electricity demand during high/peak demand period.

## Power equation for hydropower

Micro Hydro Power (MHP) uses mechanical energy of water in streams. The energy of water in the streams in present in the form of kinetic and potential energy. Kinetic energy of water is due to its velocity of flowing water in river, and potential energy is due to its altitude relative to a provided reference.

Energy stored in water body at a height (h) above a certain reference can be expressed as

E = m g h ------------ (1)

Where,

- E = energy of water in Joules

- m = mass of water in kg

- g = acceleration due to gravity in m/s2 and

- h = elevation of water with respect to the sea level in m

Equation 1 can be rewritten as

E = ρ x V x g x h [(kg/m3) x (m3) x (m/s2) x m]	[where V = volume, ρ = density of water]

= 1000 x V x g x h [kg x (m/s2) x m]

= 1000 x V x g x h [N x m]

= 1000 x V x g x h [J]

So, the power can be calculated as

P	 = E/t [J/s]

= 1000 x V x g x h/t [W]

= 1000 x (V/t) x g x h [W]

= Q x g x h [kW]			[where Q = V/t is the flow rate]

= 9.81 Q x h kW

Equation above represents the theoretical power that may be generated from elevated water. In reality some losses are involved in power generation. Let h be the efficiency of the process of power generation. Then the equation may be rewritten as

P = 9.8 x η x Q x h

Where, η = overall efficiency of the plant which depends on efficiency of each individual civil, mechanical, electromechanical, electrical components. For micro hydro plants efficiency varies from 0.5 to 0.6.

## Components of Micro Hydro Power Plants

### Civil components

  - Intake Structure

    - Used to divert water from river to headrace canal

  - Weir

    - Used to block river flow

  - Headrace canal

    - Used to divert flow from river to forebay

  - Gravel Trap

    - Used to separate gravel from diverted flow

  - Spillway

    - Used to spill excess water in headrace canal

  - Settling basin/desilting basin

    - Used to separate sand particles from diverted flow

  - Forebay Tank

    - Used to divert flow from headrace canal to penstock pipe

  - Anchor Block and support pier

    - Used to support penstock pipe

  - Powerhouse

    - Used to house all major mechanical/electrical components

  - Tailrace canal

    - Used to divert flow from turbine to river

### Mechanical components

  - Turbine

    - Used to convert kinetic energy of water to rotational energy

  - Penstock

    - To divert flow from forebay to turbine

  - Drive System

    - To drive generator using rpm of turbine

  - Expansion Joint

    - Joint provided to accommodate linear expansion of penstock pipe in varying climate temperature

  - Valves

    - Used to control flow of water from penstock to turbine

  - Trash rack

    - To block twigs, leaves, other trash entering the penstock pipe

  - Flushing system

    - To flush sand/gravel stored in desilting basin or gravel trap

### Electrical components

  - Generator

    - Used to convert rotational energy from turbine to electrical power

  - Electronic Load Controller

    - Used to maintain frequency of generator by keeping the overall load constant by distributing generator load to ballast and village

  - Transformer

    - Use to step up or step-down transmission voltage to minimize loss in transmission/distribution

  - Control Panel

    - To control the system

  - Power cable

    - To transmit the power

### Transmission/distribution components

  - Conductor

    - To transmit power from power house to village

  - Insulator

    - To provide insulation for conductor

  - Staywires

    - To support poles

  - Poles

    - To support conductors

### Protection/Control

  - Lighting arrestor

  - Earthing

  - Fuse/MCB

## Classification of Turbines

### According to basic working principle

- Impulse and reaction turbine

### According to head

- High head (Pelton)

- Medium head (Cross flow, Francis)

- Low head (Kaplan)

### According to flow directions

- Axial Flow

- Radial Flow

- Tangential flow

- Mixed Flow

## Classification of Turbines according to basic working principle

### Impulse Turbines

Major portion of potential energy of water is converted to kinetic energy before striking the turbine runner. The impulsive force imparted by high velocity jet of water on runner bucket produce a mechanical power on the turbine shaft. There is no pressure difference between inlet and outlet of the turbine runner

### Reaction Turbines

In reaction turbine the potential energy of water is mainly converted to pressure energy before striking the turbine blade. There exists pressure difference between inlet and outlet of turbine runner. The energy transformed due to decrease in pressure energy of pressure difference is known as reaction effect. In the reaction type turbines two effects cause the energy transfer from the flow to mechanical energy on turbine shaft.

First drop the pressure energy occurs as water flows from inlet to the outlet of the turbine runner. This is denoted by reaction part of the energy conversion. Secondly change in direction of the velocity vectors of the flow through passage between the runner blades transfer the impulsive force. This is denoted by the impulsive part of the energy conversion

## General features and use of impulse and reaction turbines

| Impulse Turbines | Reaction Turbines |
| --- | --- |
| - Tolerate sand | - Water is required to be clean |
| - Easy to fabricate | - Difficult and expensive to fabricate |
| - Suitable for medium to high head | - Suitable for low to medium head |
| - Efficient at wide a range of head and flow | - Poor part flow efficiency |
| - Jet of water strike the runner bucket | - Runner has to be completely filled with water and used pressure drop across turbine runner |
| - No cavitation problems | - Cavitation must be avoided |
| - Low specific speed | - High specific speed |

Common Impulse turbines: Pelton, Turgo, Crossflow

Common Reaction turbines: Francis, Propeller and Kaplan

## Importance of MHP in Nepal’s Context

- Makes use of locally available water resources

- Suitable for Nepal in case of hilly and isolated settlement where there is abundance of water resources and connection opportunity to national grid is limited.

- MHP can supply power source for operating rural cottage industries.

- People in rural area can get involved in income generation activity

- Health improvement, social and educational benefit

- Eco-friendly- less environmental adverse impact

## Limitations

- Site specific: only feasible in sites with availability of head and flow

- Long distance transmission is not suitable

- Power production is based on availability of head and flow, rather than demand which limits the power produced

# References

(2022). Retrieved November 2, 2022, from Researchgate: https://www.researchgate.net/figure/Schematic-diagram-of-a-typical-run-of-river-hydropower-system-4_fig6_258404306

Boyle, G. (2013). Renewable Energy Power For A Sustainable Future (Vol. Third Edition). Oxford: Oxford University Press.

S. Hasan, S., & Sharma, D. (2009). Non-Conventional Energy Resources. Delhi: S. K. Kataria and Sons.

Sharma, P. D. (2014). IOE Lecture Notes, Solar Energy Resources.

Singal, R. (2011). Non-Conventional Energy Resources (Vol. Third Edition). Delhi: S. K. Kataria and Sons.