\

ENERGY, ENVIRONMENT AND SOCIETY

Lecture Notes

Chapter 16

Case Study

Lecturer:

Associate Prof. Manchan Tiwari

2022, November

Learning Objectives of the Lecture:

To impart basic knowledge to undergraduate students on the topic of:

- Case study of feasibility study of Micro Hydro power of Nepal

# Summary of the project

The proposed power house site is located at Fedi village, ward no. 5 of Salpa Silicho Rural Municipality of Bhojpur district. The potential load centres of the project include: Pichhuwa, Tallo Maarel, Siraane, Siraan Tole, Pengche, Bakhuma, Thulo Tendo, Tendo, Baasemlaa etc.

The design discharge of the project is 210 lps and available gross head is 80 meters. The project is designed for the installed capacity of 100 kW, taking overall efficiency of 60.93 %. Total length of headrace canal is 1300 meters. Headrace route includes 1300 m long lined headrace canal. Settling Basin lies 10 m away from the intake region. The spillway of settling basis consists of 15 m lined canal. Penstock pipe and tailrace canal are 214 m & 30 meters respectively. Penstock pipe is proposed of 350 mm diameter and 4 mm thickness. The spillway of forebay consists of 32 m lined canal. The transmission/ distribution network consists of low-tension and high tension line. Seven transformers are proposed at various locations due to very high length of transmission line. The total conductor length for the low tension line is 139,907 m and for HT line is 85,120 m.

The total cost of the project is estimated as Rs. 58,855,870 including VAT. Thus, the cost per kW becomes Rs, 588,558.7. Similarly, costs of civil, mechanical and electrical works are estimated as Rs. 16,961,165 (28.82%), Rs 3,472,102 (5.90%) and Rs. 27,220,223 (46.25%) respectively. The cost of installation including testing commissioning, tools and spare parts is Rs. 600,000 (1.02 %) and Rs. 82,675 (0.14%) respectively. The transportation cost is estimated Rs. 3,022,401 (5.14%) and the contingency have been taken as Rs. 2,802,660 (4.76%). 13% VAT for non-local cost has been calculated as Rs. 4,694,643 (7.98%).

In general, although the project cost is relatively high, it seems that the project is technically and financially feasible. The high project cost is due to long length of transmission lines at the target beneficiary households are very far from the proposed power house location. Public interest in project implementation is high. Almost negligible negative environmental impact will occur due to the constructional activities of the MHP. There is no need of heavy deforestation and massive construction. Thus this project is strongly recommended for the installation as it is believed to provide a significant positive impact to the society in terms of awareness as well as other income generating activities thorough lighting and other end uses.

# Salient features of the project

General

Name of the project	: Salpa Community Micro Hydropower Project

Project Location	: Salpa Silicho Rural Municipality

Name of Source  	: Salpa River

Load Centre(s)  	: Pichhuma, Tallo Matel, Siraane, Siraan Tole, Pengche, Bakhuma,

Thulo Tendo, Tendo, Wasemla

Technical Features

GPS Coordinates of Intake		: 27°24' 15.1"N, 86° 58'17.3"E, Z = 1646 m

GPS Coordinates of Forebay		: 27°24' 14.5"N, 86° 58' 38.3"E, Z = 1576 m

Type of Intake				:  Orifice Type, Side Intake

Diversion 				:  Temporary Weir, 8 m long on both rivers

Gross Head 				:  80 m

Net Head  				:  76 m

Measured Flow			:  490 lps

Date of Flow Measurement		:  05/15/2022

Method used for Flow Measurement	: Salt Dilution

Design Flow				:  210 lps

Overall Efficiency			: 60.93%

Design Power				: 100 kW

Length of Headrace	 		: 1300 m lined canal

Penstock pipe				:  Mild Steel, 218 m long, 350 mm diameter, 4 mm thick

Electro Mechanical Features

Type of Turbine			: Pelton

Turbine Electrical Power Output	: 100 kW

Mechanical Transmission		: Flat Belt (Diameter of Generator Pulley: 175 mm, Diameter   of Turbine Pulley: 322 mm)

Generator				: 200 kVA (Synchronous Generator) 50Hz, 400 V, 1500 RPM

ELC     				: 100 kW

Ballast Load				:  120 kW, Ballast heaters with Water tank

Total conductor length of  HT line	:  85,120 m

Low conductor length of LT line	: 139,907 m

Source of Financing:

| S.N. | Source | Amount (Rs) | Share (%) | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Rural Municipality Subsidy | 52,970,283 | 90.00% |  |
| 5 | Local Government/ Community Contribution | 5,885,587 | 10.00% |  |
| Total Source of Finance |  | 58,855,870 | 100.00% |  |

Proposed End Uses                                    :	Huller, Communication Centre/Photocopy

Tariff for lighting                                       :	NRs 5 per watt per HH

Tariff for business use                                :	NRs. 25 per kWh

# Project Site Details

The Project site is located at Salpa Silicho Rural Municipality of Bhojpur District. Most of the load center lies beyond the range of 3 km from the powerhouse.

| District Name | Gaupalika | Tole | TOPO Sheet No: |
| --- | --- | --- | --- |
| Bhojpur | Salpa Silicho Rural Municipality |  | - |

# Geological and Environmental Aspects

The topographical features of the project were judged to be favorable for the construction work of a Micro-hydropower project. The elevation of the power house site is about 1496 meter from the mean sea level. All civil structures are located at the bushy land, barren land and some cultivated land. All the civil structures are located at the right bank of the river. According to the surface study, the terrain is stable. The terrain along the penstock route is almost steep. The project site is located in remote area. Very little development infrastructures is observed in this area. Since most of the people depend on kerosene for lighting and the forests for their fuel for cooking, the trees/bushes of the forest are being destroyed day by day. However, it is believed that after installation of Micro-hydro, the people would be aware about controlled deforestation and improve the sanitation in the area.

# Hydrology and water right issue

The river for the source of Salpa Silicho Community MHP is perennial stream. The flow of both the stream was measured following salt dilution method using conductivity meter. The flow was measured on 15th May, 2022. The flow in the river was 490 lps. The hydrological calculation is based on MIP method. The site lies on the MIP region 1. The design discharge was calculated considering about 85% of 11 month exceeding, 5% of water losses and 10% for downstream release of the total flow from both the river. 210 LPS is taken as design discharge which is more than sufficient. The average monthly flow using the MIP method is presented in the table below.

Table 1.1 : Flow availability round the year (MIP region-1)

| Month | @ river |
| --- | --- |
| January | 452 |
| February | 339 |
| March | 245 |
| April | 188 |
| May | 490 |
| June | 1131 |
| July | 2733 |
| August | 4712 |
| September | 3110 |
| October | 1508 |
| November | 773 |
| December | 584 |
| Annual average | 1355.4 |

# Energy Potentials and Energy Demands

The proposed Salpa Silicho Micro Hydro Project would supply electricity to the nearby villages. Average power demand per household has been calculated as 96.62 Watts. Moreover, the community is interested to run some end-users within the service area. The expected load demand pattern (Watt) over 24 hours period has been provided in the following table.

| S.N. | Load | Operating Time |  |  |  | Operating Parameters |  | Energy Consumption per year (kWh) | Tariff Rs. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 5 pm – 11Pm 5 am – 7 am | 7 am –3 pm | 8 am –4 pm | 9 am – 5 pm | Hours/day | Days/Year |  |  |
| 1 | Income from lighting | 100 kW |  |  |  | 8 | 330 | 264,000 | Rs. 5 /W/HH |
| 2 | Agro Processing Mill |  | 7x3 kW |  |  | 8 | 230 | 38,640 | Rs. 25/ kWh |
| 3 | Saw Mill/Rural Carpentry |  |  |  | 7x3 kW | 8 | 286 | 48,048 | Rs. 25/ kWh |
| 4 | Photocopy, Rural Communication Center |  |  |  | 7x3 kW | 8 | 286 | 43,680 | Rs. 25/ kWh |
|  | Total |  |  |  |  |  |  | 17,160 kWh |  |

# Socio Economic Condition and Affordability

The dominant ethnic groups of the project area comprise Brahmin, Janajati and Dalit. Agriculture and livestock rising are the main occupation of the people. Though, the economic condition of the people varies from poor to medium rich, the living standard of the majority people is average and below-average. In general, it is observed that most of the people could afford electricity at their required level.

The main crop is maize, millet, wheat, rice and potatoes. Some vegetable crops are also produced in the project area.

## 2.6 Availability of Construction Materials and Labor

| S.N | Particular | Availability of Materials | Remarks |
| --- | --- | --- | --- |
| 1 | Stone | Service area and Neighbors |  |
| 2 | Aggregates | Service area and Neighbors |  |
| 3 | Sand | Service area and Neighbors |  |
| 4 | Cement | Nearest roadhead |  |
| 5 | Wood | Service area and Neighbors |  |
| 6 | Wooden Pole | Service area and Neighbor |  |
| 7 | Skilled Labour | Nearest roadhead |  |
| 8 | Unskilled Labour | Service area and Neighbors |  |

## 2.7 Power Calculation

The proposed size of the Micro Hydropower scheme is 100 kW with 210 LPS design flow and an available gross head of 80 meters with overall efficiency of 60.93% for Pelton Turbine.

Power = 9.81ηHQ Where,

η= Overall efficiency of the plant

η = ηt x ηp x ηd x ηg

Where,

ηt= Turbine Efficiency = 0.700

ηp= Penstock Pipe Efficiency = 0.950

ηd= Efficiency of drive system = 0.980

ηg= Generator Efficiency = 0.9350

Therefore, η= 0.70 x 0.95 x 0.98 x 0.9350 = 60.93 %

Power = 9.81 X 0.6093 X 80 X 0.210 = 100 kW

# Civil components

## Weir/Intake/Protection Works

Intake structure is located in the left bank of the river. The flow from the river will be directed to the intake. A temporary weir will be constructed. The weir is proposed to be 0.7 m height and 8 m length which shall be constructed low cost and utilizes locally available materials which could be easily maintained after damaging by the flood during rainy seasons.

Small side intake with orifice system is recommended as the flow in the stream is shallow. The design flow for orifice is 252 lps (1.2 times of design flow for turbine). The size of the orifice is proposed to be 0.4 m x 0.7 m.  The proposed size of the trashrack is 1.8 m x 0.7 m. Flood protection wall is recommended to protect the flood entering the headrace canal.

## Settling Basin

The settling basin has been proposed at barren land, which is 35 m far from the intake. The internal size of the basin is proposed 8.0 m x 2.0 m with 1.5 m of depth. The basin is designed to flush at every 12 hours and manually. A flushing gate of size 0.5 m * 0.5 m, 1.7 m height has been proposed to remove the collected particles. Similarly, the spillway canal of same sized as the headrace canal of length 15 meter up to Kholsa is proposed from the settling basin.

Stone masonry wall with 1.3 meter base thickness and 0.30 meter at top is proposed on 1:4 C/S for the construction of the mentioned basin. Plaster of 12.50 mm thick on 1:4 c/m is proposed in wetted area of the structure. The base of the floor will be 30 cm thick stone soling and 10 cm PCC (1:2:4) on top of it.

## Headrace canal alignment

The headrace canal passes through right bank of river. The soil type along the headrace is most of common soil and little gravel mixed soil. Lined canal is proposed throughout the headrace canal alignment. Due to the topography and geological condition stone masonry canal (1:4) c/s plasters are proposed. The length and size of stone masonry canal is 1300m and 0.65 x 0.7 m including the free board of 0.3 m.

## Forebay

The Forebay has been proposed at barren land, which is 1300 m far from the intake. It is located at the end of headrace conveyance. The basin is designed to flush at every 12 hours and manually. A flushing gate of size 0.5 m * 0.5 m and 1.6 m height has been proposed to remove the collected particles. Similarly, the spillway canal of same sized as the headrace canal of length 32 meter up to Kholsa is proposed from the Forebay.

Stone masonry wall with 1.3 meter base thickness and 0.30 meter at top is proposed on 1:4 C/S for the construction of the mentioned basin. Plaster of 12.50 mm thick on 1:4 c/m is proposed in wetted area of the structure. The base of the floor will be 30 cm thick stone soling and 10 cm PCC (1:2:4) on top of it.   The design calculations show the following dimensions.

- Particle size to be removed	=	0.3 mm Ø

- Vvertical				=	0.03m/s

- Width				=	2.00 m

- Inlet transition length		=	3.25 m

- Length of the basin		= 	8.00 m

- Penstock Inlet zone		=	2.3 m x 2.0 m

- Settling zone			=	8.0 m x 2.0 m

- Length of flushing canal	=	32 m

## Penstock Alignment, Anchor Block and Support Piers

Penstock alignment has been selected on stable ground. The ground slope varies from 7° to 44 0. As the slope is steep low, the penstock length is 218 m for the gross head of 80 m. There is no single horizontal bends in penstock alignment. Eleven expansion joints have been proposed downwards of each anchor block. The total penstock of is 218 meter long and 350 mm in diameter. The proposed thickness of the penstock pipe is 4 mm for the whole length.

## Anchor Blocks:

Ten anchor blocks have been proposed in order to anchor the Penstock pipe firmly. Anchor blocks are designed as per the simple thumb rule suggested in several Micro Hydro designs manual.  The anchor block is constructed with 1:3:6 PCC with 40% plums, applying nominal reinforcement.

## Support Piers:

Fifty (50) numbers of support piers have been proposed at an interval of about 3 meters in average. The support piers are to be constructed with 1:3:6 PCC and stone masonry works in 1:6 cement sand mortar.

## Powerhouse / Machine Foundation / Tailrace

### Powerhouse:

The powerhouse is proposed at the left Bank of River. 	The outside dimension of the powerhouse building including operator's quarter is 8.85 m x 5.40 m. The powerhouse has been proposed to construct in mud mortar. 1:2:4 PCC has been proposed for flooring and 26 gauges CGI sheet for roofing. The powerhouse would be strong and sufficiently waterproof to prevent ingress of rainwater into electrical equipment.

### Machine Foundation:

Machine foundation has to make in reinforced cement concrete (1:1.5:3 RCC). Although the exact size and type of machine foundation is depend on the size of the base frame provided by the turbine manufacturer, the size of the base is estimated as 3.6 meter long and 3.6 meter wide for turbine and generator.

### Tailrace Canal:

The cross section of the tailrace canal inside the power house is 0.75 m x 0.7 m and outside the power house also 0.65m x 0.70 m with 30 m length has been proposed. Tailrace canal is proposed to be rectangular in section and would be constructed in stone masonry in 1:4 c/m. The tailrace canal inside the powerhouse has been proposed with pre-cast slabs cover. The water of tailrace is discharged into the same parent stream.

# Mechanical Components

## Penstock Pipe

The penstock pipe consists of MS pipe of 350 mm internal diameter in throughout the total length of 218 m. The proposed thickness of the penstock pipe is 4 mm for the whole length. Each length of the MS penstock pipe is proposed to be of 2.5 m lengths with 9 mm thick and 420 mm wide flange at both sides. The MS penstock pipe pieces are proposed to join with 12 mm diameter bolts. The size of the proposed bolt pieces is 12 mm x 50 mm. In every joint 8 numbers of bolts with nuts are proposed with 12 mm diameter "O" ring gasket for sealing water. The penstock should be erected from bottom to top. Air vent pipe of 50 mm diameter is proposed to be installed in penstock pipe just after the Forebay.

## Expansion Joints and Valves

### Valves:

A butterfly valve of 350 mm diameter size with adopter ahead of the turbine is proposed to regulate the flow of water in penstock pipe.

### Expansion Joints:

Eleven expansion joints of diameter 350 mm are proposed to be installed just below the each anchor blocks for adjustment of the penstock pipe from expansion and contraction due to change in temperature. Each expansion joint is capable of accommodating 50 mm change in penstock length.

## Turbine and Base Frame

Turbine is sized to at a design discharge and gross head of 0.210 m3/s and 80.00m respectively, when the reservoir is at normal operation level which results in the turbine shaft power of 120 kW. Based on the preliminary design, the turbines will have a speed of 700 rpm. So for these constraints we select Pelton Turbine.

- Type: Pelton, Single Jet

- Runner diameter/PCD (mm) - 415

- Turbine RPM - 815

- Efficiency: 70 %

- Discharge: 210.00 LPS

- Gross head: 80.00 m

- No. of buckets: 17

## Drive System

Flat belt drive with transmission ratio 1:1.84 power transmission system has been proposed for this scheme.

The proposed diameter of generator pulley is 175 mm and of turbine pulley is 322 mm.

# Electrical Components

## Generator

A generator rated to continuously deliver 100 kW power at the given site condition with the following specification is proposed.

- Size, Types & Rating - 200 kVA, Synchronous, 3 Phase, Brushless

- Voltage - 400/230 Volt

- Frequency - 50 HZ

- RPM of Generator - 1500 rpm

- Power factor - 0.8

- Generator Efficiency – 93.5 %

- No of Pole of Generator – 4

- Maximum Temperature - 19ºC

The generator size and type is compatible with the electronic regulation system. The construction and bearings are rated to withstand runaway speed of the turbine.

50 kVA, self-excited, self-regulated, compounding excitation system, 50Hz, power factor: 0.8 (lag), Ingress protection: IP 23 and 93.5 % Efficiency at Full Load Condition

## Electronic Load Controller (ELC)

Electronic Load Controller (ELC) of 100 kW is proposed for regulation of speed/frequency of electricity generated from the plant. ELC with ballast unit is proposed to control the system load such that the generator is always operating at full load. The locally made Thyrister type ELC and locally available ballast load of 120 kW is proposed.

## Ballast Heater

- Size (kW)			: 120 kW

- Phase 				: Three phase

- Minimum thickness of tank	: 3 mm

Hose pipe, hose clamps-2 nos., GI nipples 3 inch long 3 nos., 1/2-inch gate Valve, with 40 kW heaters in each phase and necessary bracings at place.

## Power Cables/MCCBs/Distribution Boxes

- 240 mm2, 4-Core Copper Cable for interconnecting generator, control panel, ELC, Ballast, Sensors etc, all complete set.

- 300 mm2, 4-Core Aluminum Cable from control panel feeder terminals (main switch) to the first pole, all complete set.

- 300 A, MCCB, Three Phases Connected at Generator Side.

- 200 A, MCCB, Three Phases Connected at Load Side.

## Earthing /Lightening Arrestors

- Copper Plate Earthing:

- No. of Earthings in powerhouse (system and equipment Earthing)  (A)	: 	2  Sets

- No. of Earthings for T&D line including first pole     (B )			:	105 Sets

- Total Earthings		(A+B)						:	107 Sets

Specification:

8 SWG Copper earth wire, 600 mm x 600 mm x 3 mm copper plate (each plate 9.65 kg) as earth electrode with necessary coal, lime, salt, nut, bolts, washer, 160 mm polythene pipe etc. all complete set. Generally, place for every 500 meter length in transmission and distribution line.

## Lightening Arrestor

- 0.5 kV, 50 HZ,  ISO 9001 Certified Manufacturer

- Total 53 nos. of 0.5 kV lightening arrestor are required

- Total 25 nos. of 9 kV lightening arrestor are required

- Generally proposed in every 500 m length in transmission and distribution line.

- In three phases line there will be three numbers and in single line there will be a single lightening arrestor used.

- Earthing is done in each place where lightning arrestors are used.

## Miniature Circuit Breaker (MCB)

Specification of Current Limiting Devices:

- Breaking Current		:	0.5 A or 1 A

- Operation voltage		:	230/400 V

- Rated breaking capacity	:	3-10 KVA

- Insulation Voltage		:	500V

- Operating Temperature	:	-50C to +400C

- No of Pole			:	Single

- No.				:	1035 Nos.

- Certification			: 	Manufacturer should be of ISO Certified Company

## Energy Meter

| S. No. | Description |  |
| --- | --- | --- |
| 1. | Type | 3Phase, 4W Wye |
| 2. | Auxiliary Voltage | 140-300V AC |
| 3. | Auxiliary Power Burden | 15VA maximum |
| 4 | Frequency | 50Hz |
| 5. | Operating Voltage | 140-480V |
| 6. | Operating Current | 0-5A |
| 7. | Starting Current | 0.05% of Ib |
| 8. | Accuracy Class | 0.5 |
| 9. | Meter Constant | Programmable / Factory Set |

# Transmission and Distribution System

## ACSR Conductors / Service Wire

#### ACSR Conductors

For the transmission/distribution of the generated power, the following Aluminum Conductor Steel Reinforced (ACSR) has been proposed. Conductor sizing has been done with the consideration of anticipated peak load demand in each of the branch. The line material has been designed in such a way that maximum voltage drop at peak hours at the end of each distribution line will not exceed by 10 percent.

| Total ACSR in (m) |  |  | With Sag 10% |
| --- | --- | --- | --- |
| 1 | Squirrel | 171.63 | 188.7919 |
| 2 | Weasel | 25.74 | 28.3151 |
| 3 | Rabbit | 7.20 | 7.92 |
| Total ACSR in km |  | 205 | 225.027 |

#### Service line

All together 36,225 meter of 6 mm2 concentric Aluminum cable (@ 35m/HH) has been proposed for the service connection to the households. The internal wiring of each household should be connected through a suitable sized load-limiting switch (MCB).

## Transformers

1 step up transformer of 160 kVA is proposed for powerhouse.

7 step down transformer are proposed at various locations. The details are given below:

| Transformer | Size (kVA) | Households | Location |
| --- | --- | --- | --- |
| Transformer 1 | 15 | 92 | Fofte |
| Transformer 2 | 25 | 168 | Saano Tendo |
| Transformer 3 | 15 | 107 | Thumlung |
| Transformer 4 | 25 | 139 | Okherla Khanda |
| Transformer 5 | 15 | 105 | Pichumma |
| Transformer 6 | 25 | 187 | Siraan |
| Transformer 7 | 15 | 110 | Baralla |

## Insulators

- Small Size Shackle Insulators: 5394 numbers, Dimension (55 mm x 55 mm); Weight 200 gm; applicable in Squirrel and Service wire

- Medium Size Shackle Insulators: 1035 numbers, Dimension (75 mm x 90 mm); Weight 600 gm; applicable in Gopher, Weasel and Rabbit Conductors

## Poles

416 numbers of 6-meter long wooden poles for single phase in the scheme and 382 numbers of 7-meter long wooden poles for three phase are proposed for the scheme. The lower 1.5 m of the wooden poles should be coated with bitumen paint and buried 1 meter for wooden pole. The poles are to be erected instable soil at must be cable stayed in bends. Concrete foundation should be provided where loose/sandy soil is encountered. Details of wooden poles are given below:

7m wooden pole: Maximum span (m) = 35 m, Buried Length (m) = 1.2 m, Min. top diameter (mm) = 140 mm, Min. ground clearance (m) = 4.6 m

6m wooden pole: Maximum span (m) = 35 m, Buried Length (m) = 1 m, Min. top diameter (mm) = 125 mm, Min. ground clearance (m) = 4 m

Type										Number

7 m length wooden pole for 3 phase line	:				382 Nos

6 m length wooden pole for 1 phase line	:				416 Nos

631 numbers of 9 m steel tubular pole are proposed for the high-tension lines in the transmission system. Details of the poles is given below:

Bottom Section (5 m Long, Outer Dia. 139.7 mm, Thickness 4.85 mm), Mid-Section (2 m Long, Outer Dia. 114.3 mm, Thickness 4.5 mm) and Top Section (2 m Long, Outer Dia. 88.9 mm, Thickness 3.25 mm), Ground Clearance 6.1 m

8 numbers of H-Pole sets are proposed for 8 transformers proposed for the scheme. The details of the H-Pole are given below:

Bottom Section (5 m Long, Outer Dia. 139.7 mm, Thickness 4.85 mm), Mid-Section (2 m Long, Outer Dia. 114.3 mm, Thickness 4.5 mm) and Top Section (2 m Long, Outer Dia. 88.9 mm, Thickness 3.25 mm), Ground Clearance 6.1 m with Transformer Platform, Drop out fuse/Lightening Arrestor Fitting Channels and Accessories

## Stay Sets

159 numbers of low tension stay sets and 126 numbers of high tension stay sets are proposed. Length of Stay rod (1.8 m), dia. (16 mm), Ultimate Tensile Strength (4500 kg/Sq.mm.), Minimum Breaking Load (7272 kg),Length of Threaded Portion (300 mm), Thimble Shape (Suitable for 7/22 SWG Stay Wire), Minimum Thimble Section (18 SWG), Stay Plate Section (600 mm x 600 mm x 3 mm MS Plate), Eyebolt Length mm/1 (300 mm), Stay Wire (7/12 SWG Steel Wire, 700 Grade, 45 ton Steel Quality, 2.64 mm dia. Minimum Wt. /km (300 kg), Applicable Standard (B.S. 183 1972/(1983))

## Tools and Spare parts

### Tools

Typical tools sets are proposed as following (but not limited)

| SN | Description of work | Quantity | Unit |  | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1 | Digital Clamp Meter | 1 | Nos. |  |  |
| 2 | Spanner | 1 | Set |  |  |
| 3 | Slide Wrench | 1 | Nos. |  |  |
| 4 | Screw Driver Set | 1 | Set |  |  |
| 5 | Line Tester | 1 | Nos. |  |  |
| 6 | Allan Key Wrench | 1 | Nos. |  |  |
| 7 | Hammer 2.5 LBS | 1 | Nos. |  |  |
| 8 | Insulation Tape | 20 | Nos. |  |  |
| 9 | Aluminum Folding Ladder | 1 | Set |  |  |
| 10 | Wire Puller (2 Ton) | 1 | Set |  |  |
| 11 | Grease Gun | 1 | Nos. |  |  |
| 12 | Safety Helmet | 10 | Set |  |  |
| 13 | Hand Gloves | 20 | Set |  |  |
| 14 | Safety Boot | 10 | Set |  |  |

The exact numbers of each item and also some additional items depends on the size of power plant and its transmission and distribution nature.

### Spare parts

| S.N. | Particulars | Nos. | Unit | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Grease | 2 | kg. |  |
| 2 | Glass Fuse and HRC Fuse | 3 | Nos. |  |
| 3 | Thyrister | 3 | Nos. |  |
| 4 | Turbine Bearing | 2 | Nos. |  |

Even more spare parts can also be recommended depending upon the necessity and the size of power plant.

All the agencies included in the MHP survey should have safeguard systems that screen planned interventions to determine their potential level of environmental and social risk leading to an appropriate level of assessment and management.

# Environmental Safeguard Guidelines

- Use a screening process for  MHP, as early as possible, to determine the appropriate extent and type of environmental assessment (EA) so that appropriate studies are undertaken proportional to potential risks and to direct, and, as relevant, indirect, cumulative, and associated impacts. This helps to ensure the environmental and social soundness and sustainability of MHPs.

- Assess potential impacts of the proposed MHP on physical, biological, socio-economic and physical cultural resources, including potential impacts on human health and safety.

- Involve stakeholders, including project-affected groups and local nongovernmental organizations, as early as possible, in the preparation process and ensure that their views and concerns are made known to decision makers and taken into account. Continue consultations throughout project implementation as necessary to address EA-related issues that affect them.

- Do not finance natural forest harvesting or plantation development that would involve any conversion or degradation of critical forest areas or related critical natural habitats.

- Avoid significant conversion or degradation of critical natural habitats, including those habitats that are (a) legally protected, (b) officially proposed for protection, (c) identified by authoritative sources for their high conservation value, or (d) recognized as protected by traditional local communities.

- 10% of the least flow should be released downstream of intake at river as low flow

- Provide measures to link the environmental assessment process and findings with studies of economic, financial, institutional, social and technical analyses of a proposed project.

# Social Safeguard Guidelines

When identifying and designing a project, safeguards should help assess the potential social risks and impacts (positive or negative) associated with a development intervention. Safeguards should help define measures and processes to effectively manage risks and enhance positive impacts. The process of applying safeguard policies can be an important opportunity for stakeholder engagement and increasing ownership.

Identify marginalized group in a community through socio-economic survey and find out if the MHP component lies in their land. If YES then, has the community compensated that loss in a justified way? As marginalized group has very limited access to resources in a village, it is important to identify, assess, and address the potential economic and social impacts of the project that are caused by involuntary taking of land (e.g., loss of assets (land) or access to assets, loss of income sources or means of livelihood, whether or not the affected person must move to another location).

A under privilege group/ Women can be encouraged to participate in income generating activities promoted by MHP endues by providing subsidy which focuses on poverty alleviation of these groups.

It is equally important to pay particular attention to the needs of vulnerable groups especially those below the poverty line, the landless, the elderly, women and children, Indigenous Peoples, ethnic minorities and provide them opportunities to participate in the process of developing and implementing the procedures for determining eligibility for compensation benefits and for establishing appropriate and accessible grievance mechanisms.

For Salpa Silicho Community MHP, Environmental and social safeguard analysis was done where all the relevant information was collected using a Questioner addressing these issues during DFS survey. Following conclusions were drawn:

# Environmental Safeguard

- 10 % of low flow was considered for downstream release during hydrological calculation

- Structures of MHP do not lie on conservation/ Protected area.

- During the transmission line survey, key plan was designed and drawn to exclude the area of community forest. For this local community assisted the study team during the survey.

- These is least possibility of MHP components causing natural hazard (Landslides, deforestation)

# Social Safeguard

1035 beneficiary households have been identified during socio-economic survey. Some of these households are eligible for GESI subsidy. Moreover, MHP components do not lie on private land and hence cause not threat to the community.

During the social economic survey community with least monthly income have also been identified. End Uses proposed for Salpa Silicho Community MHP are focused to address these marginalized groups.  It is recommended that the concerned local authority and the government also provide valuable input to uplift their living standard via these endues.

It is also recommended that the community itself play a lead role in understanding the financial status of the beneficiary household and collect the required cash for the project accordingly. If the financially weak are not able to contribute cash, special considerations are to be made but it is not recommended to exclude these households from electricity.

To address the issues of women in the community, they have been encouraged to take part in User committee.

# Cost Estimates

## Summary of Project Cost

The total cost for the project is NRs. Five Crores Eighty Eight Lakhs Fifty Five Thousands and Sixteen Rupees.

## Income

| S.N. | No of HHs | Power (kW) | Operating Days | Operating Months | Total Energy Consumption (kW) | Tariff (Rs./Watt/Month) | Total Income (Rs.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1035 | 100 | 30 | 11 | 264,000 | 5.00 | 6,000,000 |  |

# Potential End –Uses

The proposed MHP is designed to produce 100 kW of electrical power. The generated power will be transmitted to households of Salpa Silicho Gaupalika. The power will be utilized for household lighting in night. The area is also potential for agricultural production and hence the power can be used in agro-processing activities during the daytime and other commercial application by the time passes.

## Agro- processing

Agro-processing will be one of the promising businesses in the village. Traditional waterwheels are very slow and time consuming, which are very inefficient and used mostly for grinding proposes. Similarly, the existing diesel mills are also expensive. To meet the ever-increasing demand for agro-processing, mechanically driven processing units is suggested for the establishment. During end use analysis, the agro processing plant is selected on the basis of local product considering the villages near to this MHP as well as production in the adjoining villages those who wish to go for processing. For these purpose seven mills of 3 kW each, seven rural carpentry of 3 kW and 7 rural communication center of 3 kW respectively is proposed.

| S.N. | Type of Business | No | Capacity (kW) | Operating Hours | Total Energy Consumption (kWh) | Tariff (Rs.) per kWh | Total Income (Rs.) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Agro Processing Mill | 7 | 3 | 8 | 38640 | 25.00 | 966,000 |
| 2 | Saw Mill/Rural Carpentry | 7 | 3 | 8 | 48048 | 25.00 | 1,201,200 |
| 3 | Rural Communication Center | 7 | 3 | 8 | 43680 | 25.00 | 1,092,000 |

# Source of Financing

| S.N. | Source | Amount (Rs) | Share (%) | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Rural Municipality Subsidy | 52,970,283 | 90.00% |  |
| 5 | Local Government/ Community Contribution | 5,885,587 | 10.00% |  |
| Total Source of Finance |  | 58,855,870 | 100.00% |  |

# References

Boyle, G. (2013). Renewable Energy Power For A Sustainable Future (Vol. Third Edition). Oxford: Oxford University Press.

Chmielewski, A. G. (1999). Environmental Effects of Fossil Fuel Combustion. Warszawa: Institute of Nuclear Chemistry and Technology.

Energy Education. (2022). Retrieved November 14, 2022, from https://energyeducation.ca/encyclopedia/Fuel_cell

S. Hasan, S., & Sharma, D. (2009). Non-Conventional Energy Resources. Delhi: S. K. Kataria and Sons.

Sedhai, S. (2015 ). IOE Notes on EES. Institute of Engineering, Central Campus.

Singal, R. (2011). Non-Conventional Energy Resources (Vol. Third Edition). Delhi: S. K. Kataria and Sons.

Wikipedia. (2022). Retrieved November 14, 2022, from https://en.wikipedia.org/wiki/Electric_battery