## Slide 1: Renewable Energy and Distributed Generations
Lecture 1
Power Systems Planning Basics
Lecturer: Teshome Goa (Assist. Prof.)
Lecture learning outcomes:
At the end of this lecture you will be able to:
Define power system planning
Explain the objective of power system planning
Define the load forecasting
Identify the types of load forecasting

## Slide 2: Introduction
Power system is one of the largest man-made network that comprises different equipment's starting from generation to consumers
Running this very large system is a real difficult task.
It has caused numerous problems that need engineering solutions from educational sectors and Industries
For planning's, lessons should be taken from the past, present and future trends
Accordingly, the term planning is defined as the actions required for the future based on the past and recent trends.

## Slide 3
Power system planning is a process in which the aim is to decide on new as well as upgrading existing system elements, to adequately satisfy the loads for predicted future.
The elements that needs planning are;
Generation facilities
Substations
Transmission lines
Capacitors/Reactors/Controllers
Introduction Cont. …

## Slide 4
The main objectives of power system planning are:
Generating an adequate energy for satisfying the demands at low price, efficient conversion system with low environmental and social impacts
Transmitting the generated energy through long distances to the load centres at low price, more efficient, stable and reliable conditions.
Distributing the power or energy considering quality service, low price and efficient utilization of the energy.
Accordingly, power system planning is defined as;
Power system Planning is optimization of facilities necessary to provide adequate electrical energy in a power system network at a least cost, low environmental and social impacts through which a sustainable energy supply to customers is attained.
  Introduction cont..

## Slide 5
It is defined as determining the future trend of energy consumption based on the the base year and past trends.
It determines the total annual consumption as well as its discissions in to local and interconnection power pool loads.
It depends on:
the historical and current data of the base year
GDP
Population growth
customers’ income growth
government plan on rural electrification
Government policies and climate issues etc.
1.1 Load Forecasting:

## Slide 6
Why Load forecasting is needed?
There is a time lag between awareness of a future need and serving that need.
Having the forecasted load, the power utility company should thinks about an adequate power generation, transmission and distribution system facilities and other circuit protective devices.
However, delivering requires long-time in terms of construction of generation and transmission facilities
Thus, the time lag is the main reason for forecasting and planning.
Power system planning starts with a forecast of projected future load requirements.
Load forecasting Cont.….

## Slide 7
1.1. load forecasting Cont.….
Prior to load forecasting the knowledge on:
Load Classification and Characteristics of Loads,
Load Curves and Load duration curves
Demographic data
Forecast Methodologies are needed.

## Slide 8
Classification and Characteristics s of Loads
Loads are classified into
  Residential,
  commercial,
  industrial,
  agricultural,
  public services
Classification of customers for forecasting purposes would be made by
  Types of Use,
  Level of Use,
  Rate of Schedule, or
  Geographic Area.
Classification of loads

## Slide 9
The agricultural sector includes energy demand for low and medium scale agro-industries and farming.
The public service sectors may include schools, medical centres, street lighting, public offices and entertainments.
Other can include government offices, electric utility own consumption, power pool interconnections, electric railways, etc.
Classification of loads is important to study the group behaviour as load behaviour for the different groups varies significantly.
Within the broad class mentioned, further subdivisions or sub-sectors maybe defined as follows
Classification of load Cont.….

## Slide 10
Characteristics of Loads
In most part of the world, the residential loads have the most seasonal fluctuations, responsible for the seasonal variations of the system peak.
This is mostly due to the climate sensitive devices that used for space heaters and air conditions.
In some countries, the climate condition does not significantly vary throughout the year. Therefore seasonality demand is minimal.

## Slide 11
Again in some parts of the world, commercial and public services loads are characterized by seasonal fluctuations just like that of the domestic category.
In countries like east Africa, there is no significant demand seasonality.
However, seasonality is common in Asian countries, Europe and USA
On the other hands, the industrial loads are considered as a base load that contain little weather dependent.
Therefore, the planning should consider seasonality
Characteristics of Loads cont.…

## Slide 12
  Load Curves and Its duration curves
Load curve is a graphical representation between load in kW/MW in proper time sequence and times. It shows the variation of load on the power station.
The highest point on the load curve represents the maximum demand (peak demand) on the station on that day.
The area under the load curve gives the total energy supplied on that day.
If this area is divided with the number of hours gives the average load (power) on the station.
Load curves can be daily, weekly, monthly and yearly depending on the period of observation.
For daily load curve, the period of time is taken as 24 hours and for annual load curve the time is considered as (24*365)=8760 hours.

## Slide 13
Load duration curve:
Defined as representing the loads in descending magnitude, that is, with the greatest load at the left, lesser loads towards the right and the lowest load at the extreme right.
It is derived from the load curve, represents the same data as load curve.
Load duration curve determines the % of system peak load.
Load duration curve helps in deterring the average load or average demand as given by:
Average Load= Total Energy/Total Hours
It is the ratio of energy consumed in a given period of the time in hours.

## Slide 14
Load factor of a system is the ratio of the average load over a given period of time to the maximum demand (peak load) occurring in that period.
Load Factor=Average Load/Peak Load
It would be ideal to have a flat load curve. In practice, load curves are far from flat. For a flat load curve, the load factor will be higher.
Higher load factor means more uniform load pattern with less variations in load.
This is desirable from the point view of maximum utilization of associated equipment which is selected on the basis of maximum demand.
Ethiopia’s power system has a load factor of around 0.57 (in 2006) and 0.7(2014). The industrialized countries have a load factor higher than this.
This means, the power system operates at an average 57% of the peak system load in the year 2006 and 70% in year 2014.
Load Factor:

## Slide 15: Other Important Terms and Factors for load forecasting are
Connected load. It is the sum of continuous ratings of all the equipment's connected to supply system.
The sum of continuous ratings of all the equipment's in the consumer’s premises is the “connected load” of the consumer.
For instance, if a consumer has connections of five 1000-watt lamps and a power point of 500 watts, then connected load of the consumer is 5 × 1000 + 500 = 5500watts.

## Slide 16
Maximum demand : The largest of all the demands that have occurred at a given period (say a day) is known as maximum demand.
Maximum demand is generally less than the connected load because all the consumers do not switch on their connected load to the system at a time.
The knowledge of maximum demand is very important as it helps in determining the installed capacity of the station.
The station must be capable of meeting the maximum demand.

## Slide 17
Demand factor. It is the ratio of maximum demand on the power station to its connected load i.e.,
The value of demand factor is usually less than 1.
Example: If the maximum demand on the power station is 80 MW and the connected load is 100 MW, then demand factor = 80/100 = 0·8.
The knowledge of demand factor is vital in determining the capacity of the plant equipment.

## Slide 18
Load factor. The ratio of average load to the maximum demand during a given period is known as load factor i.e.

## Slide 19
Diversity factor. The ratio of the sum of individual maximum demands to the maximum demand on power station is known as diversity factor i.e.,
A power station supplies load to various types of consumers whose maximum demands generally do not occur at the same time.
Therefore, the maximum demand on the power station is always less than the sum of individual maximum demands of the consumers.
Obviously, diversity factor will always be greater than 1.
The greater the diversity factor, the lesser is the cost of generation of power.

## Slide 20
(vii) Plant capacity factor. It is the ratio of actual energy produced to the maximum possible energy that could have been produced during a given period i.e.,
The plant capacity factor is an indication of the reserve capacity of the plant.
A power station is so designed that it has some reserve capacity for meeting the increased load demand in future. Therefore, the installed capacity of the plant is always somewhat greater than the maximum demand on the plant.
Reserve capacity = Plant capacity − Max. demand

## Slide 21: Standards needed while forecasting loads are:
  Five broad categories:
  Domestic
    Demand factor: 70-100%
    Diversity factor: 1.2-1.3
    Load factor: 10-15%
  Commercial
    Demand factor: 90-100%
    Diversity factor: 1.1-1.2
    Load factor: 25-30%
  Industrial
    Small-scale: 0-20 kW
    Medium-scale: 20-100 kW
    Large-scale: 100 kW and above
      Demand factor: 70-80%
      Load factor: 60-65%

## Slide 22: Standards needed cont.…..
  Agricultural
    Demand factor: 90-100%
    Diversity factor: 1-1.5
    Load factor: 15-25%
  Other loads
    Street lights, bulk supplies, traction etc.
  Commercial and agricultural loads are characterized by seasonal variations.
  Industrial loads are base loads and are little weather dependent.

## Slide 23
Load forecasting is vitally important for the electric industry especially in the deregulated economy.
Accurate models for electric power load forecasting are essential to the operation and planning of a utility company.
Load forecasts can be divided into three Types:
Short-term forecasts, which are usually from one hour to one weeks or a year
Medium forecasts which are usually from a week to one or two years, and
Long-term forecasts which are longer than one or two year.
  1.1.1 Load Forecast Methods

## Slide 24: a. Factors Affecting load forecasting
  Time factors such as:
    Hours of the day (day/night)
    Day of the week (week day/weekend)
    Time of the year (season)
  Weather conditions (temperature and humidity)
  Class of customers (residential, commercial, industrial, agricultural, public, etc.)
  Special events (TV programmes, public holidays, etc.)
  Population
  Economic indicators (per capita income, Gross National Product (GNP), Gross Domestic Product (GDP), etc.)
  Trends in using new technologies
  Electricity price

## Slide 25: B. Driving parameters for load forecasting's
Short Term Load forecasting (STLF)
Time of the day, week
Price , special events, weather conditions
class of customer
Medium Term Load forecasting (MTLF)
Time of the day, week
Price , special events, weather conditions
class of customer
Long Term Load forecasting (LTLF)
GDP, per capita income , Trends of technology, population

## Slide 26: C. Forecasting Approaches
Naive
Moving averages
Exponential smoothing
Trend projection
Linear regression
time-series models
Associative model(end-user and econometric approach's

## Slide 27: Forecasting Approaches Cont.….
Determining the systematic relationships between loads at various points in time is the essence of time series modelling[1].
Needs only the past values, no other variables are important
Since time is the only explanatory variable, the data collection requirements of this technique are the least of any forecasting technique

## Slide 28
However, not all time series models are easy to implement.
The predictive accuracy of time series analysis varies tremendously from application to application.
For short-term forecasts of relatively large and stable systems, it can be as accurate as more elaborate models.
It is subject to extreme errors in the 10—20 year horizon required for capacity expansion planning.
Advantages of extrapolation time series method[2]:
It is the simplest type of forecast
It requires only access to basic electricity sales and peak statistics
It can be developed by the use of simple statistical models

## Slide 29
However, not all time series models are easy to implement.
The predictive accuracy of time series analysis varies tremendously from application to application.
For short-term forecasts of relatively large and stable systems, it can be as accurate as more elaborate models.
It is subject to extreme errors in the 10—20 year horizon required for capacity expansion planning.
Advantages of extrapolation time series method:
It is the simplest type of forecast
It requires only access to basic electricity sales and peak statistics
It can be developed by the use of simple statistical models

## Slide 30: Time series forecasting approaches
i. Naive Approach
Assumes demand in next period is the same as demand in most recent period
  e.g., If the February energy demand at industry K is 1000 MW, then March energy demand will be 1000MW, too
Sometimes cost effective and efficient
ii. Moving Average Method(MA)
MA is a series of arithmetic means
Demands for next period is given by;
Moving average =
∑ demand in previous n periods
n

## Slide 31: Example
January 10
February 12
March 13
April 16
May 19
June 23
July 26
Actual 3-Month
Month demand Moving Average
(12 + 13 + 16)/3 = 13 2/3
(13 + 16 + 19)/3 = 16
(16 + 19 + 23)/3 = 19 1/3
(10 + 12 + 13)/3 = 11 2/3

## Slide 32: Time series approach Cont.…
iii. Weighted Moving Average
Used when some trend might be present
Older data is less important
Weights based on experience and intuition
EXAMPLE
,
WMA
=
∑ W*D
∑ W

## Slide 33: Weighted Moving Average cont..
The weighted moving average (WMA) makes forecasts more responsive to the most recent actual occurrences (e.g., demand).
The most recent n periods are used in forecasting.
Each period is assigned a weight between 0 and 1.
The total of all weights adds up to one (1).

## Slide 34: Weighted Moving Average (using monthly demands)
Weighted Moving Average Method n=3 |  |  |  | Weights
 |  |  |  | 0.2
 |  |  |  | 0.3
Month | Sales | Forecast | Calculation | 0.5
1 | 100 |  |  | 
2 | 80 |  |  | 
3 | 90 |  |  | 
4 | 110 | 89.00 | = 0.2*100 + 0.3*80 + 0.5*90 | 
5 | 100 | 98.00 | = 0.2*80 + 0.3*90 + 0.5*110 | 
6 | 110 | 101.00 | = 0.2*90 + 0.3*110 + 0.5*100 | 
7 | 95 | 107.00 | = 0.2*110 + 0.3*100 + 0.5*110 | 
8 | 115 | 100.50 | = 0.2*100 + 0.3*110 + 0.5*95 | 
9 | 120 | 108.00 | = 0.2*110 + 0.3*95 + 0.5*115 | 
10 | 90 | 113.50 | = 0.2*95 + 0.3*115 + 0.5*120 | 
11 | 105 | 104.00 | = 0.2*115 + 0.3*120 + 0.5*90 | 
12 | 110 | 103.50 | = 0.2*120 + 0.3*90 + 0.5*105 | 
Example: Another good example
Forecast (4) = 0.2*(Demand 1) + 0.3*(Demand 2) + 0.5*(Demand 3)
Potential problem of moving average:
Increasing n smooths the forecast but makes it less sensitive to changes
Do not forecast trends well
Require extensive historical data

## Slide 35: iv. Exponential Smoothing
Form of weighted moving average[3].
  Weights decline exponentially
  Most recent data weighted most
Requires smoothing constant ()
  Ranges from 0 to 1
  Subjectively chosen
Involves little record keeping of past data
New forecast = Last forecast +  (Last actual demand – Last forecast)
Ft = Ft – 1 +  (At – 1 - Ft – 1)
Where, Ft is the new forecast
Ft – 1 is the previous forecast
 is smoothing (or weighting) constant (0 ≤ a ≤ 1)

## Slide 36: Exponential Smoothing Example
Assume: If the Predicted demand(t-1) of customer A in February was 142MW. However, the actual demand (t-1) was 153MW. Determine the new forecast (Ft) of customer A using the smoothing constant of  =0.20.
Given:
Predicted demand (t-1)= 142 MW
Actual demand = (t-1)153
Smoothing constant a = .20
Solution:
New forecast (t) = 142 + .2(153 – 142)
New forecast = 142 + .2(153 – 142)
= 142 + 2.2
= 144.2 ≈ 144 MW

## Slide 37: Choosing  Cont.…
The objective is to obtain the most accurate forecast no matter the technique
We generally do this by selecting the model that gives us the lowest forecast error
Forecast error = Actual demand - Forecast value
= At - Ft
Common Measures of Error are[4];
Mean Absolute Deviation (MAD)
MAD=
∑ |Actual - Forecast|
n
b. Mean Squared Error (MSE)
MSE =
∑ (Forecast Errors)2
n
c. Mean Absolute Percent Error (MAPE)
MAPE =
∑100|Actuali - Forecasti|/Actuali
n
n
i = 1

## Slide 38: Example:
Assume, During the last 8 months, substation D has supplied large number of customers based on the early forecasted demands. The substations Manager wants to test the forecasting method using exponential smoothing to see how well this method works in predicting the area. He has guessed that the forecast of substation unloaded in the first quarter was 175 MW.

## Slide 39: Comparison of Forecast Error
Rounded Absolute Rounded Absolute
Actual Forecast Deviation Forecast Deviation
substation with for with for
Quarter load a = .10 a = .10 a = .50 a = .50
1 180 175 5.00 175 5.00
2 168 175.5 7.50 177.50 9.50
3 159 174.75 15.75 172.75 13.75
4 175 173.18 1.82 165.88 9.12
5 190 173.36 16.64 170.44 19.56
6 205 175.02 29.98 180.22 24.78
7 180 178.02 1.98 192.61 12.61
8 182 178.22 3.78 186.30 4.30
82.45 98.62

## Slide 40: Comparison of Forecast Error
Rounded Absolute Rounded Absolute
Actual Forecast Deviation Forecast Deviation
Tonnage with for with for
Quarter Unloaded a = .10 a = .10 a = .50 a = .50
1 180 175 5.00 175 5.00
2 168 175.5 7.50 177.50 9.50
3 159 174.75 15.75 172.75 13.75
4 175 173.18 1.82 165.88 9.12
5 190 173.36 16.64 170.44 19.56
6 205 175.02 29.98 180.22 24.78
7 180 178.02 1.98 192.61 12.61
8 182 178.22 3.78 186.30 4.30
82.45 98.62
MAD =
∑ |deviations|
n
= 82.45/8 = 10.31
For a = .10
= 98.62/8 = 12.33
For a = .50

## Slide 41: Comparison of Forecast Error
Rounded Absolute Rounded Absolute
Actual Forecast Deviation Forecast Deviation
Tonnage with for with for
Quarter Unloaded a = .10 a = .10 a = .50 a = .50
1 180 175 5.00 175 5.00
2 168 175.5 7.50 177.50 9.50
3 159 174.75 15.75 172.75 13.75
4 175 173.18 1.82 165.88 9.12
5 190 173.36 16.64 170.44 19.56
6 205 175.02 29.98 180.22 24.78
7 180 178.02 1.98 192.61 12.61
8 182 178.22 3.78 186.30 4.30
82.45 98.62
MAD 10.31 12.33
= 1,526.54/8 = 190.82
For a = .10
= 1,561.91/8 = 195.24
For a = .50
MSE =
∑ (forecast errors)2
n

## Slide 42: Comparison of Forecast Error
Rounded Absolute Rounded Absolute
Actual Forecast Deviation Forecast Deviation
Tonnage with for with for
Quarter Unloaded a = .10 a = .10 a = .50 a = .50
1 180 175 5.00 175 5.00
2 168 175.5 7.50 177.50 9.50
3 159 174.75 15.75 172.75 13.75
4 175 173.18 1.82 165.88 9.12
5 190 173.36 16.64 170.44 19.56
6 205 175.02 29.98 180.22 24.78
7 180 178.02 1.98 192.61 12.61
8 182 178.22 3.78 186.30 4.30
82.45 98.62
MAD 10.31 12.33
MSE 190.82 195.24
= 44.75/8 = 5.59%
For a = .10
= 54.05/8 = 6.76%
For a = .50
MAPE =
∑100|deviationi|/actuali
n
n
i = 1

## Slide 43: Trend Projections
Fitting a trend line to historical data points to project into the medium to long-range[4]
Linear trends can be found using the least squares technique
y = a + bx
^
where y = computed value of the variable to be predicted (dependent variable)
a = y-axis intercept
b = slope of the regression line
x = the independent variable
^

## Slide 44: Trend Projections cont.…
Least Squares Method:
Equations to calculate the regression variables
b =
Sxy - nxy
Sx2 - nx2
y = a + bx
^
a = y - bx

## Slide 45: Least Squares Example
b = = = 10.54
∑xy - nxy
∑x2 - nx2
3,063 - (7)(4)(98.86)
140 - (7)(42)
a = y - bx = 98.86 - 10.54(4) = 56.70
Time Electrical Power
Year Period (x) Demand (megawatt) x2 xy
2006 1 74 1 74
2007 2 79 4 158
2008 3 80 9 240
2009 4 90 16 360
2010 5 105 25 525
2011 6 142 36 852
2012 7 122 49 854
∑x = 28 ∑y = 692 ∑x2 = 140 ∑xy = 3,063
x = 4 y = 98.86
Assume x is number of population

## Slide 46: Least Squares Example
b = = = 10.54
∑xy - nxy
∑x2 - nx2
3,063 - (7)(4)(98.86)
140 - (7)(42)
a = y - bx = 98.86 - 10.54(4) = 56.70
Time Electrical Power
Year Period (x) Demand x2 xy
2003 1 74 1 74
2004 2 79 4 158
2005 3 80 9 240
2006 4 90 16 360
2007 5 105 25 525
2008 6 142 36 852
2009 7 122 49 854
∑x = 28 ∑y = 692 ∑x2 = 140 ∑xy = 3,063
x = 4 y = 98.86
The trend line is
y = 56.70 + 10.54x
^

## Slide 47: Least Squares Example
| | | | | | | | |
2006 2007 2008 2009 2010 2011 2012 2013 2014
160 –
150 –
140 –
130 –
120 –
110 –
100 –
90 –
80 –
70 –
60 –
50 –
Year
Power demand
Trend line,
y = 56.70 + 10.54x
^

## Slide 48: Multiple Regression Analysis
If Demand Y is depends on two or more parameters[5]
y = a + b1x1 + b2x2 …
^
It is very complex and needs soft computing techniques

## Slide 49: Econometric forecasting
In this approach, initially the relationship between the load and the driving parameters is estimated.
The relationship may be nonlinear, linear; additive or in the form of multiplication.
This relationship is established based on available historical data.
Various driving parameters may be checked to find the ones that have the dominant effects.
Once this relationship is established, the future values of the driving variables (i.e. per capita income, population, electricity price, etc.) should be projected.

## Slide 50
Mostly used independent variables include:
GDP, Population, Electrified Population, Price and GDP/Cap
The dependent variables
Energy demand or Peak demand
Multiple Regression Equation
Y=f(x1, x2, x3, x4, x5)
=a+b*GDP+C*pop+d*electrified Population+e*GDP/Cap+f
Examples of economic and other variables often used to develop econometric relationships are:
  Household income
  Electricity prices (by customer group)
  Labour productivity
  Commercial sector output (by sub sector)
  Price of other fuels
  Use of other fuels (gas,oil,coal,..etc)
  Employment (by sector and subsector)
  Industrial or agricultural productivity

## Slide 51
References :
[1]. P. Villoria, H.; C. Simon de, Blas; Marinas, Collado and etl. ‘’Time series forecasting methods in emergency contexts’’. Scientific Reports. 2023, doi.org/10.1038/s41598-023-42917-1
[2]. B. Peter, J. and D. Richard, A. ‘’Introduction to Time Series and Forecasting’’. Springer. P. 1-59.
[3]. N., OkonkwoJ and N, Onoh. ‘’Improving the Econometric-based load forecasting in Nigerian Power Systems Using Exponential Smoothing Modeling Technique’’. International Institute of Advance Scholars Development. V.6(1).2023.
[4]. M. Dinesh, Reddy; R.R.K. Valley and N. Vishali. ‘’Load Forecasting using Linear Regression Analysis in Time series model for RGUKT, R.K. Valley Campus HT Feeder’’. International Journal of Engineering Research & Technology (IJERT) . Vol. 6 (5), 2017.
[5]. N., Phuangpornpitak and W., Prommee. ‘’A Study of Load Demand Forecasting Models in Electric Power System Operation and Planning’’. GMSARN International Journal. V.10(2016).

## Slide 52
Thank you !