## Slide 1: Advanced Power System Analysis
Lecture 1
Basics of Power Transmission Line components
Lecturer: Teshome Goa (Assist. Prof.)
Lecture learning outcomes:
At the end of this lecture, you will be able to:
Understand the importance of power system analysis
Identify the transmission line components
Define the transmission line conductors
Knows the importance of two-port network analysis

## Slide 2: Outlines
Introduction
Basics of Power Transmission Line component(BPTLC)
Transmission Line Conductors(TLC)
Two-port network Analysis
Summary
References

## Slide 3: 1. Introduction
Power System is a network of high tension wires/cables by which the generated Electrical power is transmitted and distributed throughout a region. Its main components are:
Generation System- Energy Conversion Methods
Transmission System- Ultra-high, Extra-high, High and Medium Voltage levels
Distribution System- Low voltage levels
The Load or Energy sink- Resistive, Capacitive and inductive Electrical devices
Power system is one of the largest man-made network that necessitates the insight knowledge's and understanding of the entire systems

## Slide 4: Introduction Cont.…
Running this very large system, which may interconnected as prenticed in Fig.1 is a real difficult task[1].
It needs the skills and understanding of its structure, network modeling, normal and abnormal operation, and the solution techniques for all problems.
Needs the problems to be solved by both the scholars, students and the industrial bodies.
Understanding of entire network is essential
Generally, power flow needs:
The basic understanding of network parameters like transmission lines, linearization of complex equations, the network analysis techniques, types of network buses.

## Slide 5
Figure 1: Ethiopian power network interconnection Plan.
Url: https://ai2-s2-public.s3.amazonaws.com/figures/2017-08-08/72b2d93ae770e42d2faf708b109285a437cd990c/26-Figure12-1.png
Introduction Cont.…

## Slide 6: 2. Basics of Power Transmission Line Component (BPTLC)
Power transmission lines are vital for transmitting electrical energy from power plants to substations and ultimately to the load centers . It comprises :
Conductors
Transmission towers
Insulators
Circuit breakers
Switches

## Slide 7: BPTLC Cont.…
Voltage regulators
Capacitors and reactors (VARs)
Grounding or earthling systems
Arrestors
Other electromechanical components

## Slide 8: 3. Transmission Line Conductors(TLC)
The design of a transmission line conductors depends on four electrical parameters[2]:
Series resistance
Series inductance
Shunt capacitance
Shunt conductance
The series resistance relies on the physical composition of the conductor at a given temperature.
Series inductance is produced by the presence of magnetic fields around the conductors, and depend on their geometrical arrangement of conductors.

## Slide 9: TLC Cont.….
The shunt capacitances are produced by the presence of electrostatic fields around the conductors, and depend on their geometrical arrangement.
Lastly, the shunt conductance exist due to the leakage currents flowing across insulators and air gaps between conductors .
Shunt conductance is mostly neglected during different power flow analysis since a leakage current is considerably small compared to nominal current.
Generally, the presences of these components, their magnitude and their impact on the network analysis varies with the network structure (two-port), the length of transmission line and its KV.

## Slide 10
a. Resistance: AC resistance of a conductor in a transmission line is determined based on the calculation of DC resistance.
Accordingly, if DC current is flowing along a rounded cylindrical conductor, the current is uniformly distributed over its cross-section area as given by;
eqn. (1)
Where; -is conductor resistivity at a given temperature (V-m)
L- conductor length (m)
A- conductor cross-section area (m2)
If AC current instead of the DC current is flowing, the conductor effective resistance is
higher due to frequency or skin effect.
TLC Cont.….

## Slide 11
Frequency Effect: The frequency of AC voltage produces a second effect on the conductor resistance due to the non-uniform distribution of current, which is known as skin effect.
The current tends to flow towards the conductor's surface as frequency rises, while the current density
falls in the middle.
The skin effect raises the effective resistance by decreasing the effective cross-section area that the current uses as given by Fig. 2.
Additionally, the presence of additional current-carrying conductors in the immediate proximity causes a slight increase in resistance[3].
TLC Cont.….

## Slide 12
Figure 2. The skin effect raises as frequency increases.
Url: https://rubadue.com/wp-content/uploads/2023/12/July-22-Blog-Post-Skin-Effect-and-Proximity-Effect-Losses.webp
TLC Cont.….

## Slide 13
Other variations in resistance are caused by
Temperature
strengthening of stranded conductors
Bundle conductors arrangement
The resistivity of any conductive material varies linearly over an operating temperature, and therefore, the resistance of any conductor suffers the same variations.
As temperature rises, the conductor resistance increases linearly, over normal operating temperatures as presented as:
eqn.(2)
Where; R2 is resistance at second temperature t2, R1 is resistance at initial temperature t1,
and T is the temperature coefficient for the particular material.
TLC Cont.….

## Slide 14
Strengthening of Bundle Conductor Effect: most of the recent transmission lines are bundled
There are two types of transmission line conductors: overhead and underground.
Overhead conductors, made of bare metal and suspended on insulators, are preferred over underground conductors because of the lower cost and easy maintenance.
Also, overhead transmission lines use aluminum conductors, because of the lower cost and lighter weight compared to copper conductors.
TLC Cont.….

## Slide 15
There are different types of commercially available aluminum conductors:
Aluminum-conductor-steel-reinforced (ACSR)
Aluminum-conductor-alloy-reinforced (ACAR)
All-aluminum-conductor (AAC)
All-aluminum alloy- conductor (AAAC). The aluminum conductor, stranded structure is presented in Fig.3
TLC Cont.….
Figure 3. stranded Aluminum conductor.
Url: https://ars.els-cdn.com/content/image/3-s2.0-B012176480X005076-gr6.gif

## Slide 16
ACSR is one of the most used conductors in transmission lines.
The purpose of introducing a steel core inside the stranded aluminum conductors is to obtain strength
A stranded conductor offers more flexibility and easier to manufacture than a solid large conductor high strength-to-weight ratio
The resistance of each wound conductor at any layer, per unit length, is based on its total length as presented in eqn.3.
eqn.(3)
Where , Rcond is resistance of the wound conductor, ‘l’ is the length of the wound conductor and ‘p’ is relative pitch of wound conductor as given by eqn.4.
eqn.(4)
TLC Cont.….

## Slide 17
Then, the parallel combination of n conductors with the same diameter per layer gives the total resistance per layer as follows:
eqn.(5)
Similarly, the total resistance of the stranded conductor is evaluated by the parallel combination of resistances per layer as presented in eqn.6 and 7.
eqn.(6)
Then, eqn.(7)
TLC Cont.….

## Slide 18
Equation 7 indicates that the total resistance of high-voltage transmission lines, which may be more than one conductor per phase reduces the total resistances for increasing the current carrying capability of conductor while reducing the corona effect
Corona effect occurs when the surface potential gradient of a conductor exceeds the dielectric strength of the surrounding air
which produces ionization in the area close to the conductor, with consequent corona losses, audible noise, and radio interference will be takes place.
TLC Cont.….

## Slide 19
Accordingly, by increasing the number of conductors per phase, the total cross-section area increases, the current capacity increases, and the total AC resistance decreases proportionally to the number of conductors per bundle
Conductor bundles may be applied to any voltage but are commonly used for high voltage as presented in Fig.4.
Figure 4. Bundled conductor in transmission line.
Url: https://studyelectrical.com/wp-content/uploads/2019/01/Bundled-Conductors-Types.jpg
TLC Cont.….

## Slide 20
b. Inductance and Inductive Reactance: A current-carrying conductor produces concentric magnetic flux lines around the conductor.
If the current varies with the time, the magnetic flux changes and a voltage is induced
Therefore, an inductance is present and defined as the ratio of the magnetic flux linkage to the cu-rrent flowing through conductor.
The magnetic flux produced by the current in transmission line conductors produces a total inductance whose magnitude depends on the line configuration
TLC Cont.….

## Slide 21
For the calculation of transmission line inductance, knowing the following parameters must be needed:
Magnetic field intensity ‘H’, Magnetic field density ‘B’ and Flux linkage ‘λ’
Consider an infinitely long, solid cylindrical conductor with radius r, carrying current I as shown in Fig.5.
Figure 5.A n infinitely long, solid cylindrical conductor with radius.
Url: https://d10lpgp6xz60nq.cloudfront.net/physics_images/MOT_CON_JEE_PHY_C26_E02_051_Q01.png
TLC Cont.….

## Slide 22
If the conductor is made of a non-magnetic material, and the current is assumed uniformly distributed (no skin effect), then the internal and external magnetic fields are generated is given in Fig.6
TLC Cont.….
Figure 6. The internal and external magnetic fields generated by conductor.
Url: https://www.researchgate.net/publication/308379950/figure/fig6/AS:668715272126475@1536445553542/Magnetic-field-produced-by-a-three-phase-transmission-line-not-to-scale.png

## Slide 23
To obtain the internal inductance, a magnetic field with radius x inside the conductor of length l is chosen, as shown in Fig. 7.
The fraction of the current Ix enclosed in the area of the circle chosen is determined by:
eqn.(8)
Figure 7. The internal magnetic field for radius x.
Url: https://www.google.com/url?sa=i&url=https%3A%2F%2Flink.springer.com%2Fchapter%2F10.1007%2F978-3-031-64691-1_5&psig=AOvVaw2iLYWS4Ue0Cvi9wI_TjfiB&ust=1742297276354000&source=images&cd=vfe&opi=89978449&ved=0CBQQjRxqFwoTCJCw4KiBkYwDFQAAAAAdAAAAABA-
TLC Cont.….

## Slide 24
Ampere’s law determines the magnetic field intensity H x , constant at any point along the circle contour as
eqn.(9)
, for non magnetic materials
The differential flux ԁϕ, enclosed in a ring of thickness dx for a 1-m length of conductor and the differential flux linkage dλ in the respective area are:
eqn.(10)
TLC Cont.….

## Slide 25
The internal flux linkage and inductance are obtained by integrating the differential flux linkage from x = 0 to x = r is given by:
eqn.(11)
Then, the external inductance is evaluated assuming that the total current I is concentrated at the conductor surface (maximum skin effect).
TLC Cont.….

## Slide 26
The external magnetic field at any point for circle of radius y, the magnetic field intensity Hy and the magnetic field density By , per unit length are:
eqn.(12)
The differential flux dϕ enclosed in a ring of thickness dy is:
eqn.(13)
TLC Cont.….

## Slide 27
As the total current I flows in the surface conductor, then the differential flux linkage dλ has the same magnitude as the differential flux dϕ.
eqn.(14)
By integrating the flux linkage from at any point D1 to D2 is given by
eqn.(15)
In general, the total external flux linkage from the surface of the conductor to any point D, per unit length is:
eqn.(16)
TLC Cont.….

## Slide 28
Then, the total flux linkage and inductance are summation of the internal and external flux linkage at any point D and given by eqn.17.
eqn.(17)
where GMR (geometric mean radius)=0.7788r
TLC Cont.….

## Slide 29
Inductance of a Two-Wire Single-Phase Line:
Consider a two-wire single-phase line with solid cylindrical conductors A and B with the same radius r, same length l, and separated by a distance D, where D > r, and conducting the same current I, as shown in Fig 8.
The current flows from the source to the load in conductor A and returns in conductor B (IA= -IB).
Figure 8. Electric magnetic field between two conductors.
Url: https://www.researchgate.net/publication/328134515/figure/fig2/AS:679156815773698@1538935011314/Two-conductors-19-in-a-as-in-Fig1-a-carrying-currents-with-similar-direction-each.jpg
TLC Cont.….
D
P

## Slide 30
One conductor's magnetic flux connects the other conductor.
The flux generated by conductor A and the flux generated by conductor B that links conductor A make up the total flux linking conductor A.
Consequently, at point P, the total flux linkage from conductors A and B is:
eqn.(18)
The expressions of the flux linkages above, per unit length, are:
eqn.(19)
TLC Cont.….

## Slide 31
The total flux linkage of the system at point P is the algebraic summation of λAP and λBp
eqn.(20)
For equal radius , the total flux linkage and inductance at infinity point are given as;
eqn(21)
TLC Cont.…

## Slide 32
Inductance of a Three-Phase Line :
Using the same approach the inductance for three phase system is developed[4].
If GMR value is the same for all conductors, the total flux linkage expression is the same for all phases and the equivalent inductance per phase is:
eqn.(22)
TLC Cont.….

## Slide 33
c. Capacitance and Capacitive Reactance[4]:
Capacitance exists among transmission line conductors due to their potential difference.
To evaluate the capacitance between conductors in a surrounding medium with permittivity , it is necessary to determine the voltage between the conductors, and the electric field strength of the surrounding.
eqn.(23)
The per phase capacitance of three phase system, is given by:
eqn.(24)
TLC Cont.….

## Slide 34
Normally, the four power system parameters are distributed in transmission line and determined using two port network while relating the sending end parameter with the receiving end parameters.
The voltage Vs and current Is at the sending end are connected to the voltage VR and current IR at the receiving end by the use of ABCD constants, as follows:
eqn.(25)
Transmission lines are divided into three categories based on the voltage levels and distance coverage they cover: short, medium, and long.
      4. Two-port Network Analysis(TPNA)

## Slide 35: TPNA Cont.….
Short transmission line: If the operating voltage is less than 20 kV and a transmission distance of less than 80 km.
In the case of a short transmission line, the effects of capacitance and conductance may be neglected
All that is left to consider are the series resistance and inductance.
While resistance and inductance are dispersed along the length of a line in reality, for short lines, the resistance and inductance are believed to be aggregated at a single location as presented in Fig.9[5].
Figure 9. Short transmission line representation.
Url: https://www.researchgate.net/figure/Short-transmission-line-model_fig1_352064823

## Slide 36: TPNA Cont.….
Based on the two-port network, the short transmission lines, sending and receiving end parameters are related as:
eqn.(26)
eqn.(27)
By substitution of eqn.26 in eqn.27:
eqn.(28)

## Slide 37
Medium transmission line: A medium transmission line is one that has a voltage of between 20 and 100 kilovolts and a length of 80 to 250 km.
Since the voltage is high, it is necessary to take the capacitance effects into consideration.
As a result, all admissions are combined at the sending, receiving, or center.
The following techniques are employed more frequently presented in Figs. 10 & 11, respectively:
Nominal T
nominal π
      TPNA Cont.…

## Slide 38
Figure 10: Nominal T-method Short Transmission line.
URL: https://media.geeksforgeeks.org/wp-content/uploads/20240418091804/Nominal-T-Method.webp
The ABCD parameter is calculated as;
Voltage at the mid-point of the line
eqn.(29)
      TPNA Cont.….

## Slide 39: TPNA Cont.….
Current in the capacitor,
eqn.(30)
Then, the sending-end current and Voltage are given by:
eqn.(31)
eqn.(32)

## Slide 40: TPNA Cont.….
Nominal π method.
According to this strategy, the complete resistance and inductive reactance are concentrated at the center of the line, while half of the total line capacitance is focused at each end as presented in Fig.11.
Figure 11. Nominal π method medium transmission line.
url: https://archive.nptel.ac.in/content/storage2/courses/108104051/chapter_2/2_4.html
Using the same procedures, the sending end voltage and current are given by:
eqn.(33)
eqn.(34)

## Slide 41: TPNA Cont.….
Long Transmission Line: Transmission lines that span more than 250 km (150 miles) are considered lengthy.
The approximation of the shunt admittance by two constant capacitors at each end of the line is insufficiently accurate for long lines.
Rather, the series impedance and the shunt capacitance need to be thought of as dispersed quantities, and the differential equations of the line should be solved to determine the voltages and currents on it.
On the other hand, a long transmission line can be modeled as a π model with modified shunt admittance Y' and series impedance Z', and calculations can be done on that model using ABCD constants for Fig.12.

## Slide 42: TPNA Cont.….
The series impedance and shunt admittance adjusted values are:
Figure 12. Long transmission line representation.
URL: https://www.myelectrical2015.com/2022/04/abcd-parameters-of-long-transmission.html#google_vignette
eqn.(35)
Where, Z is the series impedance of the line; Y is the shunt admittance of the line; d is the length of the line; γ is the propagation constant of the line:
eqn.(36)

## Slide 43: TPNA Cont.….
Where, z is the series impedance per km and y is the shunt admittance per km.
When γd decreases, the ratios tend to 1.0, transforming the model into a medium-length line model.
For a long transmission line, the ABCD constants are;
eqn.(37)

## Slide 44: Summary
Power system network is one of highly meshed the largest man-made system that needs the understanding of network parameters, the operation of intended network during normal and abnormal condition and hence requires the remedial actions
The four power system components, which are very important for the network understandings are: resistance, inductance, capacitance and conductance.
The network conductor resistance depends on the types of conductor, its geometer and environmental conditions.
The transmission lines can be categorized into three: short, medium and long based on its length and voltage ratings
The analysis used to evaluate the receiving end parameters of power network with the sending end parameters based on the transmission line type is known as Two-port network analysis

## Slide 45: References
[1]. H., Gärtner and A., Stamps. ‘’Ethiopian power grid: electrical power engineering & environment’’. Technische Universiteit Eindhoven. Pp:1-33, 2014,. https://pure.tue.nl/ws/files/4282573/778636.pdf
[2].G., Leonard. ‘’Electric Power Generation, Transmission, and Distribution: Transmission Line Parameters’’. Tylor and Francis Group, 1st edition. Pp.1-512, 2007. Doi: https://doi.org/10.1201/9781420009255.
[3]. M.Zaręba; T., Szczegielniak and P. Jabłoński. ‘’’Influence of the Skin and Proximity Effects on the Thermal Field in a System of Two Parallel Round Conductors’’. Energies 2023, 16, 6341. https://doi.org/10.3390/en16176341.
[4]. C., Francesca and R., Jordi-Roger. ‘’Calculation of the inductance of conductive nonmagnetic conductors by means of finite element method simulations’’. International Journal of Electrical Engineering & Education,. V.57(3), 2018. https://doi.org/10.1177/002072091880044.

## Slide 46
Thank you !