## Slide 1: Advanced Power System Analysis
Lecture 5
Load Flow Methods
Lecturer: Teshome Goa (Assist. Prof.)
Lecture learning outcomes:
At the end of this lecture, you will be able to:
Differentiate the Types of Load Flow Solution Techniques
Formulate the Gauss–Seidel load Flow Method
Develop Newton Raphson and Fast Decoupled Load Flow Methods
Know the effect of PQ and PV buses in Load flow analysis.

## Slide 2: Outlines
Introduction
Gauss-Seidel power flow equations
Newton-Raphson Power Flow
Fast Decoupled Power Flow
Summary
References

## Slide 3: 1. Introduction
Iterative power flow solution techniques like Gauss-Seidel, Newton-Raphson, and Fast Decoupled Load flow form the basis of power system analysis [1].
The following are the primary advantages of using iterative power flow solution approaches:
Capable of Handling Non-Linear Systems:
Phase angles and voltage magnitudes are the main causes of power flow equations' nonlinearity.
Iterative techniques are capable of accurately solving these non-linear equations, in contrast to direct
approaches, which perform better for linear systems.

## Slide 4: Introduction Cont.…
2. Better Scalability
Suitable for large-scale power systems with thousands of buses.
Techniques like Fast Decoupled Load Flow are designed to work efficiently on very large grids.
3. Increased Accuracy
Methods like Newton-Raphson provide very accurate results, especially when the system is well-conditioned and a good initial guess is used

## Slide 5: Introduction Cont.…
4. Efficient Memory
Iterative methods can be optimized to use less memory compared to solving large matrices directly.
Important for large power systems with limited computational resources.
5. Flexibility: easy to modify for:
Different types of buses (PQ, PV, slack)
Control variables (Tap changers, reactive power limits and AVR) are easily incorporated to the
iterative solutions.

## Slide 6: Introduction Cont.…
6. Modification Speed
Newton-Raphson methods that have been optimized to converge more quickly and use less calculate each iteration include Fast Decoupled Load Flow.
7. Suitable for Real-Time Uses
Iterative approaches are employed in real-time power system monitoring and control tools due of their speed and flexibility.
In general, it’s very suitable for the variable load condition that leads to power system parameter
fluctuations from the stated values.

## Slide 7: Introduction Cont.…
However, the number of steps needed to obtain actual solution's depends on the initial guess’s ,
problem size and the iterative technique used[2].
Thus, based on the named constraints, the approximate solutions can be either converge, diverge or
oscillate
But, the round-off error in all case goes on getting corrected in each step.
The iterative process is then repeated till the bus voltage converges with in prescribed accuracy

## Slide 8: 2. Gauss-Seidel Power Flow (G-S)
The gauss-seidel method is an iterative algorithm for solving a set of non linear load flow equations.
It is an iterative solution of power flow equations and simplest load flow solution
There are two approaches for G-S power flow analysis
When PV bus is absent
Considering all buses
Case-1:Consider G-S power flow when PV-bus is absent and algorithm of Power flow for PQ bus only[3].
PV buses are absent means there is n – 1 buses or PQ buses, and slack bus only.

## Slide 9: G-S Cont.…
Steps in computing G-S methods for PQ bus only is:
Step 1. Form the bus admittance matrix of the network by direct inspection method, formulate Ybus
matrix.
Step 2. If the slack bus is not specified, select one of the generator buses as the slack bus. The voltage
at the slack bus is assumed as Vi = 1 + j0.0
Step 3. Assume initial values of voltages for all buses except the slack bus. Vi (0) = 1 + j0.0
Step 4. Set convergence criterion, ε. If the largest of absolute of the residues exceeds the convergence
criterion, the process is repeated, otherwise it is terminated.

## Slide 10: G-S Cont.…
Step 5. Set iteration count k = 0.
Step 6. Bus count i = 1. If ‘I’ is the slack bus, then there will be an increment in the bus count.
Step 7. Solve the voltage equation for bus i as we know that.
eqn.(1)
Which is similar that:
eqn.(2)

## Slide 11: G-S Cont.…
Thus,
eqn.(3)
Accordingly, the iterative solution of power flow are given by:
eqn.(4)
Step 8: Calculate the change in bus voltage ΔVi:
Δ Vi = Vi(k+1) –Vik eqn.(5)

## Slide 12: G-S Cont.…
Step 9: The process of convergence in G-S method is slow as it requires large number of iterations to
obtain the solution.
It can be speeded up using acceleration factor.
eqn.(6)
Step 10: Calculate the bus voltages Vik+1 for all the buses except the slack bus, i = 2,3, ….,n.
Step 11: Repeat the iteration until the required solution achieved.
Step 12: Finally calculate the power flow and power losses at slack bus using the load flow equations.

## Slide 13: G-S Cont.…
Case 2: when PV bus is considered, the steps used are
Step 1: Calculate the imaginary part or reactive power of PV bus 1st using the eqn.7 for Q value.
eqn.(7)
For the given value of reactive power minimum and maximum limit:
eqn.(8)
If Qi is within the limits indicates that with available reactive power generation, it is possible to maintain the voltage magnitude at the named bus and only angle δi is calculated

## Slide 14: G-S Cont.…
δi is calculated using the expression for voltage as presented before.
Thus, the presented attempts from Step-1 to Step-12 in PQ bus also works for PV buses.
However, if Q is less than the minimum limit and greater than the maximum lit , consider the PV bus as a PQ bus.
Thus, reactive power demand is equal to the Qmin if the calculated value is less than minimum demand
The reactive power demand is equal to the Qmax if the calculated value is greater than maximum
demand

## Slide 15: G-S Cont.…
Then, the steps from Step-1 to Step-12 is applied at the same manner to determine the voltage angle of PQ bus.
It means that the voltage controlled bus is treated as a load bus with the known quantities as PD and
QD and unknown quantities as |V| and δ
Qi outside the limits, if the reactive power limits are not satisfied indicates that the voltage level at that
bus can not be maintained at the specified value.
Because, the available Q always determine the voltage at that bus.

## Slide 16
Advantages and Disadvantages of Gauss–Seidel Method A. Advantages • The calculations are simple and so there is less programming task to perform. • The memory requirement is small. • Useful for the small systems.
Faster computation per iteration compared to some other methods
G-S Cont.…

## Slide 17
Disadvantages • Requires a large number of iterations to converge. • Not suitable for large systems. • Convergence time increases with the size of the system.
Highly depends on the initial guess
G-S Cont.…

## Slide 18: 3. Newton-Raphson Power Flow (NRPF)
The Newton–Raphson method is regarded as the most crucial of the many load flow analysis solution
techniques available for big interconnected power systems.
There are numerous benefits associated with the Newton-Raphson method.
When compared to the other processes, its convergence properties are comparatively strong.
When sparse network equations are solved using the scarcity programmed ordered elimination
technique, significantly short computation times are obtained.

## Slide 19: NRPF Cont.….
The reliability of the Newton–Raphson method is comparatively good, since it can solve cases that
lead to divergence with the other popular processes, but the method is by no means reliable
Failure does not occur on some ill-conditioned problems.
The number of iterations required to obtain a solution is independent of the system size, but more
functional evaluations are required at each iteration.
Since in the load flow problem real power and magnitude of bus voltage are specified for the PV buses, the load flow equation is formulated in the polar form

## Slide 20: NRPF Cont.….
● N-R iterative method approximate set of non-linear simultaneous eqns. to set of linear simultaneous eqns. By Taylor’s expansion[4]:
Let’s consider: eqn.(9)
Where, K1 and K2 are constants.
x1(0) and x2(0) are estimate solution and We designate
Δx1(0) & Δx2(0) to correct the solution, so we can write:
eqn.(10)

## Slide 21: NRPF Cont.….
Now we can solve for Δx1(0) & Δx2(0) by expanding eqn.10. in Taylor’s series to give:
eqn.(11)
If partial derivatives of first order only taken, the above equations in matrix form:
eqn.(12)

## Slide 22: NRPF Cont.….
Equation 11, can be written as
eqn.(12)
Where, J(0) is called Jacobean of initial estimate and by finding it we can determine Δx1(0) & Δx2(0).
By correcting the initial estimate we have;
eqn.(13)
Then, the process is repeated until the correction is small
To use the above discussion for power flow problem, we choose polar coordinate and designate:
eqn.(14)
We have

## Slide 23: NRPF Cont.….
From this;
eqn.(15)
J(i) consists of the partial derivatives of P & Q with respect to each variables(voltage and its angle )
For 3 bus system if bus 1 is swing, matrix eqns. for each iteration is :
eqn.(16)
J1
J2
J3
J4

## Slide 24: NRPF Cont.….
Elements of Jacobean matrix J1:
The diagonal elements are:
eqn.(17)
The off-diagonal elements are:
eqn.(18)

## Slide 25: NRPF Cont.….
Elements of Jacobean matrix J2 :
The diagonal elements are:
eqn.(19)
The off-diagonal elements are:
eqn.(20)

## Slide 26: NRPF Cont.….
Elements of Jacobean matrix J3:
The diagonal elements are:
eqn.(21)
The off-diagonal elements are:
eqn.(22)

## Slide 27: NRPF Cont.….
Elements of Jacobean matrix J4 :
The diagonal elements are:
eqn.(23)
The off-diagonal elements are:
eqn.(24)
Difference in scheduled to calculated power (power residuals) is given by :
eqn.(25)
Then, the new estimate for voltage and its angle are: eqn.(26)

## Slide 28: NRPF Cont.….
Δδk and Δ|Vk| found from the eqn.26 is added in pervious value to calculate new value of P & Q, and
process is repeated until desired precision index achieved.
To achieve quick convergence, N-R is sensitive for initial estimate.
As initial estimate, the nominal voltages values can be used.
For PV bus J with respect to constant V will be omitted & row with respect to Q also omitted as presented in eqn.26, and both parameters are calculated after convergence.

## Slide 29: NRPF Cont.….
The steps applied for N-R power flow problem are as follow:
Step-1: Determine: eqn.(27)
Where;
Step-2: Calculate Jacobean matrix:
eqn.(28)
Step-3: Solve the following equation to find Δδ(i) and ΔV(i)
eqn.(29)

## Slide 30: NRPF Cont.….
Step 4: Power flows and losses on the network branches are computed as follows once bus voltages and angles have been solved for:
Network branches include transformers and transmission cables.
A branch element's (shown on a medium length line) direction of positive current flow is defined.
Each branch end has a set power flow.
Step 5: Lastly, determine the slack bus's real and reactive power.

## Slide 31
Advantages and disadvantages of NR method
i. Advantages
Fast convergence as long as initial guess is close to solution
large region of convergence
Used in the most actual power network analysis
ii. Disadvantages:
it requires the derivative of the function and may struggle with convergence if the derivative is zero or
the initial guess is poor.
Each iteration takes much longer than a Gauss Seidel iteration
more complicated to code, particularly when implementing sparse matrix algorithms
NRPF Cont.….

## Slide 32: 4. Fast Decoupled Load Flow (FDLF)
One of the enhanced techniques, the Fast Decoupled Load Flow (FDLF) method, was developed by simplifying the Newton–Raphson method.
This approach became the most popular in load flow analysis because of its quick convergence, dependable results, and ease of computation.
FDLF, however, does not always converge well in situations with high R/X ratios or excessive loading (low voltage) at some buses.
In these situations, numerous attempts and advancements have been made to get over
these convergence barriers.

## Slide 33: FDLF Cont.…..
Some of them focused on systems with low voltage buses, while others aimed to converge systems with high R/X ratios.
But one of the most recent innovations is a Robust Fast Decoupled Load Flow, which solves the low bus voltage and high R/X ratio problems at the same time.
It is based on generic voltage normalization techniques and heuristic justification.
This technique takes advantage of the power system's characteristic whereby the true power flow-voltage a
eqn.(30)

## Slide 34: FDLF Cont.…..
The transmission lines have high X/R ratio
For such system the real power changes ΔP are less sensitive to changes in the voltage magnitude and are most sensitive to change in phase angle Δδ.
Similarly the reactive power changes ΔQ is less sensitive to change in angles Δδ and is mainly dependent on changes in voltage magnitude:
Which means , the J2 = J3=0

## Slide 35: FDLF Cont.…
It is given as :
eqn.(31)
FDLF technique is very useful in contingency analysis where numerous
outages are to be simulated or a load flow solution is required for online control.

## Slide 36: Summary
This lecture note is presents the importance of iterative power flow solutions to get the four power system parameters.
Accordingly, the load flow equations for different types of iterative power flow solution are developed
Besides this, the importance of initial guess, the size of problem and techniques used are the main points while using iterative power flow solutions. Thus, the power flow result either converge, diverge or oscillate based on these parameter effect.
The advantage of Fast-decoupled load flow solution is also discussed.
Finally, the advantage and disadvantage of each power flow solution techniques are
also discussed.

## Slide 37: References
[1]. Ch., Romil; R., Naresh; M., Kenedy and A.,Ankit. "A streamlined and enhanced iterative method for analyzing power system available transfer capability and security ‘’. Electric Power Systems Research. V.223, 2023. doi: https://doi.org/10.1016/j.epsr.2023.109528.
[2]. M., Höger; M., Siranec and J., Altus. "Power Flow Analysis of Networks with Loads of Constant Current - Constant Power Factor Type“. 20th International Scientific Conference on Electric Power Engineering (EPE),Czech Republic, 2019, pp. 1-4, doi: https://doi.org/10.1109/EPE.2019.8777975.
[3]. A., Nigam; K., Sharma ; M., Bilal and etl. ‘A two-part alternating iteration power flow method based on dynamic equivalent admittance’’. International Journal of Electrical Power & Energy Systems. V.59,2024. https://doi.org/10.1016/j.ijepes.2024.110064.
[4]. H., Le Nguyen. "Newton-Raphson method in complex form [power system load flow analysis“. IEEE Transactions on Power Systems, vol. 12(3), pp. 1355-1359,1997, doi:10.1109/59.630481.

## Slide 38
Thank you !